## High side
SCHEDULE OF QUANTITIES
GENERAL NOTES :
1 | All items of work under this Contract shall be executed strictly to fulfill the requirements laid down under “Basis of Design” in the specifications. Type of equipment, material specification, methods of installation and testing and type of control shall be in accordance with the specifications, approved shop drawings and the relevant Indian Standards, however capacity of each component and their quantities shall be such as to fulfill the above mentioned requirement.
2 | The rate for each item of work included in the Schedule of Quantities shall, unless expressly stated otherwise, include cost of:
a. All materials, fixing materials, accessories, appliances tools, plants, equipment, transport, labour and incidentals required in preparation for and in the full and entire execution, testing, balancing, commissioning and completion of work called for in the item and as per Specifications and Drawings.
b. Wastage on materials and labour.
c. Loading, transporting, unloading, handling/double handling, hoisting to all levels, setting, fitting and fixing in position, protecting, disposal of debris and all other labour necessary in and for the full and entire execution and for the job in accordance with the contract documents, good practice and recognize principles.
d. Liabilities, obligations and risks arising out of Conditions of Contract.
e. All requirements of Specifications, whether such requirements are mentioned in the item or not. The Specifications and Drawings where available, are to be read as complimentary to and part of the Schedule of Quantities and any work called for in one shall be taken as required for all.
f. In the event of conflict between Schedule of Quantities and other documents including the Specifications, the most stringent shall apply. The interpretation of the Consultant/Project Manager shall be final and binding.
3 | All equipments, quantities and technical data indicated in this Schedule are for the Contractor’s guidance only, these are based on the documents prepared by the Services Consultant. This schedule must be read in conjunction with other documents. The Contractor shall be paid for the actual quantity of work executed by him in accordance with the approved Shop Drawings at the contract rates.
4 | This Schedule shall be fully priced and the extensions and totals duly checked. The rates for all items shall be filled in INK including NIL items.
5 | No alteration whatsoever is to be made to the text or quantities of this Schedule unless such alteration is authorised in writing by Services Consultant. Any such alterations, notes or additions shall, unless authorized in writing, be disregarded when tender documents are considered.
6 | In the event of an error occurring in the amount of the Schedule, as a result of wrong extension of the unit rate and quantity, the unit rate quoted by the tenderer shall be regarded as firm and the extensions shall be amended on the basis of rates.
7 | Any error in totaling in the amount column and in carrying forward total shall be corrected. Any error, in description or in quantity, omission of items from this Schedule shall not vitiate this Contract but shall be corrected and deemed to be variation required by the Consultant/Project Manager.
8 | The Contractor shall procure and bring Materials/Equipment to the site only on the basis of drawings approved for construction and shop drawings and not on the basis of Schedule of Quantities which are approximate only. This also applies to the Contractor’s requisition for Owner supplied materials.
9 | The unit rate for all local equipment or materials in Indian Rupees shall include cost of equipment and materials including all taxes and duties and also including forwarding, freight, insurance and transport into Contractor’s store at site, storage, installation, testing, balancing, commissioning and other works required.
Item | Description | [7 empty] | Unit | Qty | Rate | Amount
A. | EQUIPMENT
1 | Supplying of double skin construction draw thru type AIR HANDLING UNITS as per specification, each complete with following :-
a. | Supply air centrifugal Forward curved fan with efficiency >65%
b. | VFD designed for HVAC applications for supply air fan with built-in PID controller, control panel (keypad & display) , IP-55 enclosure for use on standard centrifugal fans. The VFDs should not cause any deration of the connected motors and must ensure that class B temperature levels of the connected motors are never exceeded. The display should be in alpha-numeric characters and programming facility should be in user-friendly HVAC terminology. VFD’s shall have builtin harmonic filters.
Each VFD panel to be provided with digital display showing electrical parameters like voltage, current and power consumption.
Each VFD shall be installed in a dedicated external IP-55 enclosure and the inter connecting wires between driver and MCC shall be included.
c. | Coil of copper tube and aluminum construction sized at maximum face velocity of 500 fpm.
d. | Pre Filter ( MERV-8 ) in supply air stream
e. | Squirrel cage induction motors suitable for 415 ± 10% volts, 50 Hz, AC supply & high efficiency.
f. | Fan belt drive package
g. | Vibration isolators and SS 304 drain pan
h. | Fan outlet velocity not exceeding 10 mps.
i. | Height of Ceiling Suspended AHU shall not exceed 700 mm.
| Tag No. | Floor Space |  | CFM | TR | Max (HP) | Minm Total Static (mm) | Cooling/Heating Deep Coil(row)
Basement
| AHU-01 | Hall |  | 2100 | 4 | 1 | 40 | 6 | No. | 1
| AHU-02 | Restaurant |  | 3000 | 5 | 0.5 | 40 | 6 | No. | 2
| AHU-03 | House keeping, Linnen & locker |  | 3700 | 6 | 3 | 50 | 6 | No. | 0
| AHU-04 | Bar sitting area |  | 3300 | 6 | 3 | 50 | 6 | No. | 0
Ground Floor
| AHU-05 & 06 | All day dinning |  | 4000 | 10 | 3 | 50 | 6 | No. | 2
| AHU-07& 08 | All day dinning(Floor Mounted) |  | 4000 | 11 | 3 | 50 | 6 | No. | 2
| AHU-9 | Reception, front office & reservation |  | 4400 | 8 | 3 | 50 | 6 | No. | 1
| AHU-10 | GM office, Dir. Office, Mr. Ashok office etc. |  | 3700 | 9 | 0.5 | 40 | 6 | No. | 1
First Floor
| AHU-11 | Office Area |  | 5500 | 15 | 1.5 | 40 | 6 | No. | 1
Terrace Floor
| AHU-12 | TFA AHU for Fresh air |  | 6500 | 48 | 3 | 50 | 8 | No. | 1
Note :
Quoted price shall include the following:
i. AHU- 12 shall be provided with thermal break profile.
ii. AHU- 12 shall be provided with 8 row deep coil.
iii. AHU-01,02,03, 04, 05, 06 ,09, 10, & 11 shall be suitable for ceiling mounted.
iv. All AHU’s shall be supplied with hydrophillic coating on fins
v. Frame-work for coils of all AHU’s shall be SS-304 construction.
vi. AHU- 05,06, 07, 08, 09, 10 & 11 shall be provided with VFD.
vii. AHU- 07, 08, & 12 shall be suitable for Floor mounted.
2 | Supplying of vertical / horizontal FAN COIL UNITS, blow through type, each complete with 3 row deep chilled water coil, one or more 3 speed centrifugal fans, cleanable metalic filters,SS-304, main condensate drain pans, auxillary drain pan, as described in specifications, casing, coil piping connections, through copper pipes, condensate drain connections, wiring, control wiring in conduit upto thermostat boxes. All fan coil units shall be suitable for 220 + 6% volts, 50 cycles, single phase power supply. Fan Coil Units shall be of following refrigeration capacities as listed.
| 1.5 TR nominal capacity 600cfm | [7 empty] | No. | 1
| 2.0 TR nominal capacity 800cfm | [7 empty] | No. | 2
| 2.5 TR nominal capacity 1000cfm | [7 empty] | No. | 1
3 | Supplying of CHW Cassette type fan coil unit, blow through type, each complete with 3 row deep chilled water coil, one or more 3 speed centrifugal fans, cleanable metalic filters,SS-304, main condensate drain pans, auxillary drain pan with condensate drain pump, as described in specifications, casing, coil piping connections, through copper pipes, condensate drain connections, wiring, control wiring in conduit upto thermostat boxes. All fan coil units shall be suitable for 220 + 6% volts, 50 cycles, single phase power supply. Fan Coil Units shall be of following refrigeration capacities as listed.
| 1.0 TR nominal capacity -400cfm | [7 empty] | No. | 3
4 | Supplying, of IN LINE FANS fixed in AHU fan section suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. Quoted price shall be inclusive of electronic speed regulator and wiring between fan & speed regulator for single phase fans. Incase of 3 phase fans quated price shall be inclusive of DOL starter panel with cabling between starter panel and fan. The incoming power supply to speed regulator / starter panel shall be provided by electrical contractor.
| Tag No. |  | Decription |  | Location |  | CFM
| IF-1 |  | Toilet Exhaust |  | Terrace |  | 2500 |  | No. | 1
| IF-2 |  | Fresh air |  | Ground Floor |  | 1150 |  | No. | 0
5 | Supply, installing, testing and commissioning of ceiling/wall mounted AIR COOLED SPLIT AIR CONDITIONING UNITS as described in specifications. The unit shall be complete with cabinet type fan coil unit and external condensing unit, complete in all respects, inclusive of copper refrigerant piping, inclusive of copper refrigerant piping, GI condensate drain piping, valves and insulation. Quoted price shall include cost of thermostat, wiring, control cooling thermostat, wiring, control wiring , control wiring and earthing.
All units listed below shall be provided with cooling / heating thermostat. Wiring & conduiting between theremostat and unit shall be included in quoted price. The unit capacities shall be as follows :
| 1.0 TR -400cfm Split air conditioning units as described above | [7 empty] | No. | 3
TOTAL CARRIED TO SUMMARY