## SUMMARY
PROJECT: RENOVATION OF HOTEL CLARKS - LUCKNOW
PACKAGE: Fire Alarm & PA System
S.NO. | DESCRIPTION OF WORKS | FAS WORKS (INR) | TOTAL (INR)
I | SUPPLY, INSTALLATION, TESTING & COMMISSIONING OF THE WORKS AS PER SPECIFICATIONS
A | Supply
B | Installation
SUB TOTAL-I (EXCLUSIVE OF TAXES & DUTIES)
II | TAXES & DUTIES
Transportation upto site
Custom Duty
GST
SUB TOTAL-II (TAXES & DUTIES)
TOTAL (I+II) (INCLUSIVE OF TAXES & DUTIES)
COMPREHENSIVE AMC (INCL. ALL TAXES)

## FAS
PROJECT: RENOVATION OF HOTEL CLARKS- LUCKNOW.
PACKAGE: Fire Alarm & PA System.
Sl.No. | Description | Unit | Qty | Total Supply (INR) |  | Installation (INR) |  | Total (INR)
|  |  |  | Rate (INR) | Amount(INR) | Rate (INR) | Amount (INR) | Rate (INR) | Amount (INR)
A | SUPPLY, INSTALLATION, TESTING & COMMISSIONING OF THE FOLLOWING AS PER SPECIFICATION.
SECTION - I : FAS SYSTEM SHOULD BE UL LISTED
1 | CONTROL PANEL : Location - Security Control Room
1.1 | Supply of Microprocessor based Networkable Analogue Addressable FACP with 6 loops. Minimum 127 detectors per loop. LCD display, built-in RS-232 interfaces for programming via a PC and serial printer interface • 5 on board programmable Form C relays rated at 1 amp at 30VDC (Fire1, Fire2, trouble, supervisory, aux.) • 500mA of auxiliary power available rated at 24 VDC • 500 network wide software zones • Network Capability of up to 64 panels • Auto-learn feature • Fire Drill test function • Walk Test function • Alarm Verification feature Powerful & versatile Cause & Effect programming (up to 500 maximum, network wide) including: *Cause & Effect action, *Disable function configuration *Test mode configuration | Nos. | 1
a | BMS integration communication card ( Bacnet IP protocol) | Nos. | 1
1.2 | Supply, installation, testing & commissioning of graphical illustration display software with PC Connectivity & dotmatrix alarm printer for Fire detection system | Nos. | 1
1.3 | Intel Core i7@ 3.0 GHz
8 GB of RAM DDR3
1TB SATA II hard drive for OS and Security Center applications
1 GB PCI-Express dual-head video adapter
1024 x 768 or higher screen resolution
100/1000 Ethernet Network Interface Card
DVD+/- RW Drive
Windows 7, 64 bit with all licenses
Dual Monitor Support
| 21" TFT monitor | Set | 1
1.4 | Fire Alarm Active Repeater Panel (Location: Engineering, Front office ) | Nos. | 2
SUB TOTAL FOR CONTROL PANEL
2 | DEVICES
Following analog addressable devices compatible with the control panel covered above
2.1 | Supply of Analogue Addressable Multisensor Detector, including base Simple and reliable device addressing method, Automatic compensation for sensor contamination, Two built-in power/alarm LED's, Programmable Non-polling LED's, Non-directional smoke chamber, Vandal resistant security locking feature complete as required. | Nos. | 88
2.2 | Supply of Analogue Addressable Rate of Rise Heat detector, including base Simple and reliable device addressing method, Automatic compensation for sensor contamination, Two built-in power/alarm LED's, Programmable Non-polling LED's, Non-directional smoke chamber, Vandal resistant security locking feature complete as required. | Nos. | 3
2.3 | Supply of Analogue Addressable Multisensor Detector with in built sounder, including base Simple and reliable device addressing method, Automatic compensation for sensor contamination, Two built-in power/alarm LED's, Programmable Non-polling LED's, Non-directional smoke chamber, Vandal resistant security locking feature, complete as required. | Nos. | 0
2.4 | Supply of Analogue Addressable CO Detector, including base Simple and reliable device addressing method, Automatic compensation for sensor contamination, Two built-in power/alarm LED's, Programmable Non-polling LED's, Non-directional smoke chamber, Vandal resistant security locking feature, complete as required. | Nos. | 0
2.5 | Supply of Analogue Addressable Beam Detector, including base Simple and reliable device addressing method, with reflector complete as required. | Nos. | 0
2.6 | Supply, installation, testing and commissioning of Control Relays shall be complete with Pilot Relay for Tripping of Third Party Equipment, suitable for switching 5A/15A current through the Relay contacts , MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling as per technical specification & drawings. The CR will be connected to AHU for tripping, Electrical system for tripping, Elevator Management,music sysytem, fire suppression system in kitchen and gas bank for alarm | Nos. | 13
2.7 | Supply, installation, testing and commissioning of Control Module shall be complete with Pilot Relay for control of Third Party Equipment, suitable for switching 5A/15A current through the Relay contacts , MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling as per technical specification & drawings. The CM will be connected to pressurisation fans, smoke exhaust fans, PA etc. | Nos. | 9
2.8 | Supply, Installation, Testing & Commissioning of Addressable Monitor Module with all mounting accessories, complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling. | Nos. | 12
2.9 | Supply, installation, testing & commissioning of Response Indicator (for above False Ceiling Detector) with matching screws complete with GI Junction box, Cable lugs at cable end and ferruling as per technical specification. | Nos. | 0
2.1 | Supply, installation, testing & commissioning of Addressable Manual Pull Station with Address Switch and all mounting accessories , complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling as per technical specification. | Nos. | 6
2.11 | Supply, installation, testing & commissioning of Hooters/Sounder with Light Strobe(min 100 Candela) including modules with minimum 4 distinct sound patterns to indicate Exit doors and direct occupants for safe and fast evacuation , complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling.as per technical specification. | Nos. | 12
2.11A | Supply, installation, testing & commissioning of Light Strobe(min 100 Candela) including modules to indicate Exit doors and direct occupants for safe and fast evacuation , complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling.as per technical specification. | Nos. | 4
2.12 | Supply, installation, testing & commissioning of Fault Isolator as per technical specification. | Nos. | 2
2.13 | Supply, installation, testing & commissioning of LPG gas detector with panel & module with built in sounder as per technical specification. | Nos. | 0
2.14 | 2 way communication Fire Fighter's Telephone Jack with module as per specifications complete as required. | Nos | 6
2.15 | 2 way communication Fire Fighter's Handset | Nos | 2
2.16 | Suuply, installation, testing and commissioning of induct smoke detector with housing and assembly etc. | Nos | 0
2.17 | Supply, Installation, Testing & Commissioning of Addressable Monitor Module with Magnetic Contact concealed type for monitoring final exit doors all mounting accessories, complete with MS Powder coated Junction Box for mounting on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling. | Nos | 2
SUB TOTAL FOR DEVICES
3 | WIRING ACCESSORIES FOR FDA SYSTEM
Supply Installation Testing of Wiring including junction box and end Terminations for the following
3.1 | 2CX 1.5Sq.mm, shielded Copper conductor, Armoured cable FRLS grade PVC insulated flexible WIRE(2hrs. Fire rated - minimum) | Mtrs | 4770
SUB TOTAL FOR WIRING ACCESSORIES
TOTAL FOR SECTION I
SECTION - II
4 | PA SYSTEM
4.1 | Supply, installation, testing and commissioning of rack mounted Booster Amplifier 2X240 W | SET | 1
4.2 | Supply, installation, testing and commissioning of one of the approved make ceiling/wall mounted multi tap speakers of 3/6 W rated power handling capacity, in-built line matching transformer, wide opening angle, complete with all mounting accessories as per specifications. | Nos | 48
4.3 | Microcontroller Based 24 Zone Selector with Following features, (a) Feather type key pads to select the zones. (b) Moulded plastic attractive enclosure. (c )Backlight LED Display (d) User friendly interactive display. (e) Announcement selector - PTT Switch. (f) Listen selector switch. (g) All Call switch to select all zones simultaneously for announcement (h) Built in auto change over Ul certified for over ride the music. (i) Pre recorded voice evacuation system. (j) Shall be ingrated with Fire Alarm system. Controller Unit with (a) Built-in Power supply. (b) Zone Selector Switching Circuit (c)Terminal blocks to terminate zones ,wires, amplifier wires etc., (d) Built-in Power Supply for TB Speaker (e) CALL Monitoring Circuit (f) Additional terminal blocks for CALL & Mic signal Gooseneck Microphone ( Fitted in the Console ) (Should be able to add 4 Additional Zones if required) | Nos. | 1
4.4 | Supply, installation, testing and commissioning of rack mounted Mixer Amplifier with minimum 6 inputs. | Nos | 1
4.5 | Supply, installation, testing and commissioning of rack mounted CD Player with USB & MP3 including pre recorded fire evacuation msg. | Nos | 1
4.6 | Supply, installation, testing and commissioning of 29 U Rack | Nos | 1
4.7 | Supply, installation, testing and commissioning of rack mounted Mixer Amplifier 60 W | Nos | 1
4.8 | Supply, installation, testing and commissioning of Podium Mic with on/off and selector switch. | Nos | 2
SUB TOTAL FOR TWO WAY COMMUNICATION SYSTEM
5 | WIRING
Supply Installation Testing of Wiring including end Terminations for the following
5.1 | 2C x 1.5 sq mm Twin twisted, PVC sheathed, armoured copper Cable suitable for PA & Music system. | Mtrs | 4450
5.2 | Multi core Mic cable , PVC sheathed, Un-armoured copper Cable. | Mtrs | 300
SUB TOTAL FOR WIRING
TOTAL FOR SECTION - II
A | TOTAL FOR SECTION - I + II
B | TAXES
Transportation upto site
Custom Duty
VAT
TOTAL FOR TAXES - B
Grand Total (C = A+B)